## PSR PSALM Edit (2)
MINDANAO GENERATION
(PSALM PORTFOLIO)
FOR : | MR. LARRY I. SABELLINA |  |  |  |  | MR. DENNIS EDWARD A. DELA SERNA |  | MR. ARNOLD C. FRANCISCO
| VP, Mindanao Generation |  |  |  |  | President and CEO, PSALM |  | VP - PAMG, PSALM
PLANT STATUS REPORT
as of 0800H Friday, 13 February 2026
PLANT NAME | Rated Capacity (MW) | Nominated | Available Capacity (MW) |  | Lake Lanao Projected Ave. Outflow | Load at 0800H | REMARKS |  | PRIMARY STORAGE OF HYDRO HEPs | [12 empty] | INPUT From JMM-DCM/CPN
[9 empty] | Lake/Dam | Level (m) | Remarks | [10 empty] | today Friday, 13 February 2026
[9 empty] | Lake Lanao | 701.20 | Normal | [10 empty] | INPUT 1
|  | Capability | [6 empty] | Agus 2 Forebay | 637.30 | [11 empty] | Total load @ 0800H.xls |  | 650.80 MW
AGUS 1 | 80 | 0 | 80 | 0 |  | 52000 | Lake Lanao Elevation is 701.50 m.a.s.l. |  | Agus 4 Forebay | 358.50 |  |  | GATE#1 | GATE#2 | GATE#3 | GATE#4 | GATE#5 | GATE#6 | ELEVATION | [6 empty] | AGUS1 Lake Lanao Elevation
unit 1 | 40 | 0 | 40 |  |  | 25500 | Forced outage: 1.0h |  | Agus 5 Forebay | 242.80 |  |  | GATE#1: 0.100; GATE#2: 0.100 |  | 701.190 |  | Plant | Rated | Available | Load | Pulangi 4 Reservoir Levels
unit 2 | 40 | 0 | 40 |  |  | 26500 | Forced outage: 1.0h |  | Agus 6 Forebay | 199.80 |  |  | GATE#1: 0.000; GATE#2: 0.000 |  | 637.800 | Mr. Dennis | AGUS1 | 80 | 80 | 0 | Agus 2-7 Forebay Elevations
AGUS 2 | 180 | 180 | 180 | 0 |  | 79500 | Lake Lanao Elevation is 701.50 m.a.s.l. |  | Agus 7 Forebay | 34.60 |  |  | GATE#1: 0.500; GATE#2: 0.000 |  | 358.800 |  | AGUS2 | 180 | 180 | 0 | Note: Forebay elevations are
unit 1 | 60 | 60 | 60 |  |  | 25500 | Forced outage: 1.0h |  | Pulangi IV Reservoir | 283.50 |  |  | GATE#1: 0.550; GATE#2: 0.000; GATE#3: 0.100 |  | 243.300 |  | AGUS4 | 158.1 | 158.1 | 0 | maintained at normal levels.
unit 2 | 60 | 60 | 60 |  |  | 26500 | Forced outage: 1.0h | [5 empty] | 0.200 | 0.200 | 0.200 | 0.000 |  |  |  | 199.800 |  | AGUS5 | 55 | 55 | 0 | Spillage occurs when needed.
unit 3 | 60 | 60 | 60 |  |  | 27500 | Forced outage: 1.0h |  | HYDRO INFLOW/OUTFLOW (cms) |  |  |  | GATE#1: 0.000; GATE#2: 0.000; GATE#3: 0.000 |  | 34.100 |  | AGUS6 | 219 | 219 | 0 | RIPARIAN FLOW | CMS/MV | CMS
AGUS 4 | 158.1 | 105.4 | 0 | 0 |  | 0 | Lake Lanao Elevation is 701.50 m.a.s.l. |  | Plant | Inflow | Outflow | Remarks | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |  | Dependable Capacity = Pmax |  | AGUS7 | 54 | 54 | 0 | AGUS 1 | 0.85 | 85.0
unit 1 | 52.7 | 0 | 0 |  |  | 0 | No data |  | Lake Lanao | 0.00 | 0.00 | [10 empty] | PULANGI4 | 255 | 255 | 0 | AGUS 2 | 0.90 | 90.0
unit 2 | 52.7 | 52.7 | 0 |  |  | 0 | No data |  | Agus 1 | 0.00 | 0.00 | [10 empty] | STEAG1 | 105 | 105 | 0 | AGUS 3 | 0.88 | 88.0
unit 3 | 52.7 | 52.7 | 0 |  |  | 0 | No data |  | Agus 2 | 0.00 | 0.00 | [10 empty] | PMGPP1 | 0 | 0 | 0 | AGUS 4 | 0.92 | 92.0
AGUS 5 | 55 | 55 | 0 | 0 |  | 0 | Lake Lanao Elevation is 701.50 m.a.s.l. |  | Agus 4 | 0.00 | 0.00 | [10 empty] | PMGPP2 | 0 | 0 | 0 | AGUS 5 | 0.87 | 87.0
unit 1 | 27.5 | 27.5 | 0 |  |  | 0 | No data |  | Agus 5 | 0.00 | 0.00 | [14 empty] | AGUS 6 | 0.89 | 89.0
unit 2 | 27.5 | 27.5 | 0 |  |  | 0 | No data |  | Agus 6 | 0.00 | 0.00 | [14 empty] | AGUS 7 | 0.91 | 91.0
AGUS 6 | 219 | 165 | 0 | 0 |  | 0 | Lake Lanao Elevation is 701.50 m.a.s.l. |  | Agus 7 | 0.00 | 0.00 | [10 empty] | Rated | Available | C @0800H Load |  | MLRD GATES OPENING
unit 1 | 34.5 | 20 | 0 |  |  | 0 | No data |  | Pulangi IV | 0.00 | 0.00 | [10 empty] | AGUS1 | 80 | 80 | 0 | Status: Operational
unit 2 | 34.5 | 21 | 0 |  |  | 0 | No data | [14 empty] | AGUS2 | 180 | 165 | 120
unit 3 | 50 | 42 | 0 |  |  | 0 | No data |  | GENERATION DATA (MWh) | [12 empty] | AGUS4 | 158.1 | 158.1 | 105.4 | SPILLAGE (MCM) INPUT 2
unit 4 | 50 | 38 | 0 |  |  | 0 | No data |  | Plant | Today | MTD | YTD | [9 empty] | AGUS5 | 55 | 55 | 55 | Lake Lanao | 0.00
unit 5 | 50 | 44 | 0 |  |  | 0 | No data |  | AGUS1 | 0 | 990 | 990 | [9 empty] | AGUS6 | 219 | 219 | 165 | Agus 2 | 0.00
AGUS 7 | 54 | 54 | 0 | 0 |  | 0 | Lake Lanao Elevation is 701.50 m.a.s.l. |  | AGUS2 | 0 | 990 | 990 | [9 empty] | AGUS7 | 54 | 54 | 54 | Agus 4 | 0.00
unit 1 | 27 | 27 | 0 |  |  | 0 | No data |  | AGUS4 | 0 | 0 | 0 | [9 empty] | PULANGI4 | 255 | 255 | 215 | Agus 5 | 0.00
unit 2 | 27 | 27 | 0 |  |  | 0 | No data |  | AGUS5 | 0 | 0 | 0 | [9 empty] | Total | 1001.1 | 986.1 | 714.4 | Agus 6 | 0.00
TOTAL AGUS | [8 empty] | AGUS6 | 0 | 0 | 0 | [13 empty] | Agus 7 | 0.00
PULANGI IV | 255 | 215 | 255 | 0 |  | 5700000 | Reservoir Elevation is 290.00 m.a.s.l. |  | AGUS7 | 0 | 0 | 0 | [13 empty] | Pulangi IV | 0.00
unit 1 | 85 | 75 | 85 |  |  | 1850000 | Forced outage: 0.5h. Normal operation |  | PULANGI4 | 5,700 | 61,650 | 61,650 | [9 empty] | Rated | Available | C for day % Pmax |  | INPUT 2
unit 2 | 85 | 70 | 85 |  |  | 1900000 | Normal operation |  | Total NPC | 5,700 | 63,630 | 63,630 | [9 empty] | AGUS1 | 80 | 80 | 0 | ↓
unit 3 | 85 | 70 | 85 |  |  | 1950000 | Excellent operation | [14 empty] | AGUS2 | 180 | 165 | 66.67 | PROCESS
TOTAL HYDRO | [8 empty] | CAPACITY FACTOR (%) | [12 empty] | AGUS4 | 158.1 | 158.1 | 66.67
Agus-Pulangi Forecasted Load @ 6pm, Feb 13, 2026 : Agus = 500.8 MW & Pulangui IV = 150.0 MW, Total Load: 650.8 MW | [8 empty] | Plant | Today | MTD | YTD | [9 empty] | AGUS5 | 55 | 55 | 100
MCFPP (STEAG), unit 1 | 116 | 105 | 105 | 61.5 |  |  | Normal Operation |  | AGUS1 | 0.0 | 4.1 | 4.1 | [9 empty] | AGUS6 | 219 | 219 | 75.34
MCFPP (STEAG), unit 2 | 116 | 105 | 105 | 62.6 |  |  | Normal Operation |  | AGUS2 | 0.0 | 2.3 | 2.3 | [9 empty] | AGUS7 | 54 | 54 | 100
TOTAL IPP | 232 | 210 | 210 | 124.1 |  |  |  |  | AGUS4 | 0.0 | 0.0 | 0.0 | [9 empty] | PULANGI4 | 255 | 255 | 84.31
TOTAL NPC-PSALM | 1,233.10 | 1,021.3 | 857.00 | 759.59 |  |  |  |  | AGUS5 | 0.0 | 0.0 | 0.0
[9 empty] | AGUS6 | 0.0 | 0.0 | 0.0
| NPC-PSALM Capacity Mix | [5 empty] | MinGen Forecasted Load Share (MW), @6pm Today |  | AGUS7 | 0.0 | 0.0 | 0.0
Hydro | 811.31 | [7 empty] | PULANGI4 | 93.1 | 91.6 | 91.6
Coal Fired Thermal | 210 | [7 empty] | Average | 13.3 | 14.0 | 14.0
[5 empty] | AGUS 1 | 60
[5 empty] | AGUS 2 | 120
[5 empty] | AGUS 4 | 96
[5 empty] | AGUS 5 | 40
[5 empty] | AGUS 6 | 144.8
[5 empty] | AGUS 7 | 40
[5 empty] | PULANGI IV | 150
■ Hydro ■ Coal Fired Thermal
Note:
1. Dependable Capacity (DC) is the maximum capacity, modified for ambient limitations for a specific period of time, such as month or a season.
2. Available Capacity (AC) is the dependable capacity, modified for equipment limitations for any time.
3. The usual occurrence of Peak is at 1200H.
4. AGUS 5 HEP gate no. 2 clogged at 0.10m for Nawlach Pulp Inc. (NPI) plant water use.
MCFPP (STEAG) | TYPE OF CONTI IPP OPERATOR END OF COOPERATION PER CONTRACTED INDICATIVE BID
MGPP | BOT/IPPA | STEAG State Pov | 16-Nov-31 | 200.00 2017 (Subject to DOE's policy direction)
| IPPA AA | FDC | 11-Dec-17
Note:
1. The Available Capacity in this report includes equipment limitation and water outflow consideration based on the 2020 Lake Lanao Operating Guide Curve.
2. AGUS 6 HEP, units 1 & 2 up-rated from 25 MW to 34.5 MW each and rated speed increased from 200 to 225 rpm effective February 1, 2020.
3. AGUS 2 HEP is limited to 120 MW total load to prevent risk of flooding at lakeshore areas and Balo-i plains as per Environmental Compliance Certificate dated January 14, 1992.
4. AGUS 5 HEP gate no. 2 clogged at 0.10m for Nawlach Pulp Inc. (NPI) plant water use.
5. The usual occurrence of Peak is at 1800H.
6. Forecast inflow of Lake Lanao is stable and operating at Normal Stage.
7. Agus 6 HEP: 18cms of water spilled due to partially opened spillway gate no. 1.
Prepared by: |  |  | Checked and Reviewed by: |  |  | Checked and Reviewed by: |  | Approved by:
O.M. LAVA |  |  | JMM MATA |  |  | EL ADIONG |  | C.C. AMIGABLE JR.
Prin. Engr. A, GPD |  |  | Manager, GPD |  |  | Acting Manager, GPD |  | Dept. Manager, GPD
Prepared by: |  |  | Checked and Reviewed by: |  |  | Checked and Reviewed by: |  | Approved by:
D.R.B. CAIRO |  |  | JMM MATA |  |  | EL ADIONG |  | DB ESMADE JR.
Prin. Engr. B, GPD |  |  | Manager, GPD |  |  | OIC-Dept Manager, GPD |  | Acting Dept. Manager, GPD
Agus 2 HEP is limited to 40 MW/per unit due to water constraints as per Environmental Compliance Certificate "that Agus 2 shall not be operated at full capacity..." This is to prevent risk of flooding at lakeshore areas and Baloi plains.
AGUS 1 | 80 | 80 | 0
AGUS 2 | 180 | 180 | 120
AGUS 4 | 158.1 | 158.1 | 105.4
AGUS 5 | 55 | 55 | 55
AGUS 6 | 219 | 219 | 165
AGUS 7 | 54 | 54 | 54
PULANGI IV | 255 | 255 | 215
AGUS 1 | 80 | 80 | 0
AGUS 2 | 180 | 180 | 0
AGUS 4 | 158.1 | 158.1 | 0
AGUS 5 | 55 | 55 | 0
AGUS 6 | 219 | 219 | 0
AGUS 7 | 54 | 54 | 0
Pulangi4 | 255 | 255 | 0
STEAG 1 | 116 | 105 | 0
STEAG 2 | 116 | 105 | 0
10-Jan-25 | 0 | 0 | 0
11-Jan-25 | 0 | 0 | 0