## PSR PSALM Edit (2)
MINDANAO GENERATION
(PSALM PORTFOLIO)
FOR : | MR. LARRY I. SABELLINA |  |  |  |  | MR. DENNIS EDWARD A. DELA SERNA |  | MR. ARNOLD C. FRANCISCO
| VP, Mindanao Generation |  |  |  |  | President and CEO, PSALM |  | VP - PAMG, PSALM
PLANT STATUS REPORT
as of 0800H Sunday, 01 February 2026
PLANT NAME | Rated Capacity (MW) | Nominated | Available Capacity (MW) |  | Lake Lanao Projected Ave. Outflow | Load at 0800H | REMARKS |  | PRIMARY STORAGE OF HYDRO HEPs | [12 empty] | INPUT From JMM-DCM/CPN
[9 empty] | Lake/Dam | Level (m) | Remarks | [10 empty] | today Sunday, 01 February 2026
[9 empty] | Lake Lanao | 701.20 | Normal | [10 empty] | INPUT 1
|  | Capability | [6 empty] | Agus 2 Forebay | 637.30 | [11 empty] | Total load @ 0800H.xls |  | 650.80 MW
AGUS 1 | 80 | 0 | 80 | 0 |  | 52000 | Lake Lanao Elevation is 701.50 m.a.s.l. |  | Agus 4 Forebay | 358.50 |  |  | GATE#1 | GATE#2 | GATE#3 | GATE#4 | GATE#5 | GATE#6 | ELEVATION
unit 1 | 40 | 0 | 40 |  |  | 25500 | Forced outage: 1.0h |  | Agus 5 Forebay | 242.80 |  |  | GATE#1: 0.100; GATE#2: 0.100 |  | 701.190 |  | Plant | Rated | Available | Load
unit 2 | 40 | 0 | 40 |  |  | 26500 | Forced outage: 1.0h |  | Agus 6 Forebay | 199.80 |  |  | GATE#1: 0.000; GATE#2: 0.000 |  | 637.800 | Mr. Dennis | AGUS1 | 80 | 80 | 0
AGUS 2 | 180 | 180 | 0 | 0 |  | 0 | Lake Lanao Elevation is 701.50 m.a.s.l. |  | Agus 7 Forebay | 34.60 |  |  | GATE#1: 0.500; GATE#2: 0.000 |  | 358.800 |  | AGUS2 | 180 | 180 | 0
unit 1 | 60 | 60 | 0 |  |  | 0 | No data |  | Pulangi IV Reservoir | 283.50 |  |  | GATE#1: 0.550; GATE#2: 0.000; GATE#3: 0.100 |  | 243.300 |  | AGUS4 | 158.1 | 158.1 | 0
unit 2 | 60 | 60 | 0 |  |  | 0 | No data | [5 empty] | 0.200 | 0.200 | 0.200 | 0.000 |  |  |  | 199.800 |  | AGUS5 | 55 | 55 | 0
unit 3 | 60 | 60 | 0 |  |  | 0 | No data |  | HYDRO INFLOW/OUTFLOW (cms) |  |  |  | GATE#1: 0.000; GATE#2: 0.000; GATE#3: 0.000 |  | 34.100 |  | AGUS6 | 219 | 219 | 0
AGUS 4 | 158.1 | 105.4 | 0 | 0 |  | 0 | Lake Lanao Elevation is 701.50 m.a.s.l. |  | Plant | Inflow | Outflow | Remarks | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |  | Dependable Capacity = Pmax |  | AGUS7 | 54 | 54 | 0
unit 1 | 52.7 | 0 | 0 |  |  | 0 | No data |  | Lake Lanao | 0.00 | 0.00 | [10 empty] | PULANGI4 | 255 | 255 | 0
unit 2 | 52.7 | 52.7 | 0 |  |  | 0 | No data |  | Agus 1 | 0.00 | 0.00 | [10 empty] | STEAG1 | 105 | 105 | 0
unit 3 | 52.7 | 52.7 | 0 |  |  | 0 | No data |  | Agus 2 | 0.00 | 0.00 | [10 empty] | PMGPP1 | 0 | 0 | 0
AGUS 5 | 55 | 55 | 0 | 0 |  | 0 | Lake Lanao Elevation is 701.50 m.a.s.l. |  | Agus 4 | 0.00 | 0.00 | [10 empty] | PMGPP2 | 0 | 0 | 0
unit 1 | 27.5 | 27.5 | 0 |  |  | 0 | No data |  | Agus 5 | 0.00 | 0.00
unit 2 | 27.5 | 27.5 | 0 |  |  | 0 | No data |  | Agus 6 | 0.00 | 0.00
AGUS 6 | 219 | 165 | 0 | 0 |  | 0 | Lake Lanao Elevation is 701.50 m.a.s.l. |  | Agus 7 | 0.00 | 0.00 | [10 empty] | Rated | Available | C @0800H Load
unit 1 | 34.5 | 20 | 0 |  |  | 0 | No data |  | Pulangi IV | 0.00 | 0.00 | [10 empty] | AGUS1 | 80 | 80 | 0
unit 2 | 34.5 | 21 | 0 |  |  | 0 | No data | [14 empty] | AGUS2 | 180 | 165 | 120
unit 3 | 50 | 42 | 0 |  |  | 0 | No data |  | GENERATION DATA (MWh) | [12 empty] | AGUS4 | 158.1 | 158.1 | 105.4
unit 4 | 50 | 38 | 0 |  |  | 0 | No data |  | Plant | Today | MTD | YTD | [9 empty] | AGUS5 | 55 | 55 | 55
unit 5 | 50 | 44 | 0 |  |  | 0 | No data |  | AGUS1 | 1,920 | 57,600 | 115,200 | [9 empty] | AGUS6 | 219 | 219 | 165
AGUS 7 | 54 | 54 | 0 | 0 |  | 0 | Lake Lanao Elevation is 701.50 m.a.s.l. |  | AGUS2 | 4,320 | 129,600 | 259,200 | [9 empty] | AGUS7 | 54 | 54 | 54
unit 1 | 27 | 27 | 0 |  |  | 0 | No data |  | AGUS4 | 3,780 | 113,400 | 226,800 | [9 empty] | PULANGI4 | 255 | 255 | 215
unit 2 | 27 | 27 | 0 |  |  | 0 | No data |  | AGUS5 | 1,320 | 39,600 | 79,200 | [9 empty] | Total | 1001.1 | 986.1 | 714.4
TOTAL AGUS | [8 empty] | AGUS6 | 5,256 | 157,680 | 315,360
PULANGI IV | 255 | 215 | 0 | 0 |  | 0 | Reservoir Elevation is 290.00 m.a.s.l. |  | AGUS7 | 1,296 | 38,880 | 77,760
unit 1 | 85 | 75 | 0 |  |  | 0 | No data |  | PULANGI4 | 6,120 | 183,600 | 367,200 | [9 empty] | Rated | Available | C for day % Pmax
unit 2 | 85 | 70 | 0 |  |  | 0 | No data |  | Total NPC | 24,012 | 720,360 | 1,440,720 | [9 empty] | AGUS1 | 80 | 80 | 0
unit 3 | 85 | 70 | 0 |  |  | 0 | No data | [14 empty] | AGUS2 | 180 | 165 | 66.67
TOTAL HYDRO | [8 empty] | CAPACITY FACTOR (%) | [12 empty] | AGUS4 | 158.1 | 158.1 | 66.67
Agus-Pulangi Forecasted Load @ 6pm, Feb 01, 2026 : Agus = 500.8 MW & Pulangui IV = 150.0 MW, Total Load: 650.8 MW | [8 empty] | Plant | Today | MTD | YTD | [9 empty] | AGUS5 | 55 | 55 | 100
MCFPP (STEAG), unit 1 | 116 | 105 | 105 | 61.5 |  |  | Normal Operation |  | AGUS1 | 100.0 | 100.0 | 100.0 | [9 empty] | AGUS6 | 219 | 219 | 75.34
MCFPP (STEAG), unit 2 | 116 | 105 | 105 | 62.6 |  |  | Normal Operation |  | AGUS2 | 100.0 | 100.0 | 100.0 | [9 empty] | AGUS7 | 54 | 54 | 100
TOTAL IPP | 232 | 210 | 210 | 124.1 |  |  |  |  | AGUS4 | 99.5 | 99.7 | 99.6 | [9 empty] | PULANGI4 | 255 | 255 | 84.31
TOTAL NPC-PSALM | 1,233.10 | 1,021.3 | 857.00 | 759.59 |  |  |  |  | AGUS5 | 100.0 | 100.0 | 100.0
[9 empty] | AGUS6 | 98.0 | 98.5 | 98.3
| NPC-PSALM Capacity Mix | [5 empty] | MinGen Forecasted Load Share (MW), @6pm Today |  | AGUS7 | 100.0 | 100.0 | 100.0
Hydro | 811.31 | [7 empty] | PULANGI4 | 100.0 | 100.0 | 100.0
Coal Fired Thermal | 210 | [7 empty] | Average | 99.6 | 99.7 | 99.7
[5 empty] | AGUS 1 | 60
[5 empty] | AGUS 2 | 120
[5 empty] | AGUS 4 | 96
[5 empty] | AGUS 5 | 40
[5 empty] | AGUS 6 | 144.8
[5 empty] | AGUS 7 | 40
[5 empty] | PULANGI IV | 150
■ Hydro ■ Coal Fired Thermal
Note:
1. Dependable Capacity (DC) is the maximum capacity, modified for ambient limitations for a specific period of time, such as month or a season.
2. Available Capacity (AC) is the dependable capacity, modified for equipment limitations for any time.
3. The usual occurrence of Peak is at 1200H.
4. AGUS 5 HEP gate no. 2 clogged at 0.10m for Nawlach Pulp Inc. (NPI) plant water use.
MCFPP (STEAG) | TYPE OF CONTI IPP OPERATOR END OF COOPERATION PER CONTRACTED INDICATIVE BID
MGPP | BOT/IPPA | STEAG State Pov | 16-Nov-31 | 200.00 2017 (Subject to DOE's policy direction)
| IPPA AA | FDC | 11-Dec-17
Note:
1. The Available Capacity in this report includes equipment limitation and water outflow consideration based on the 2020 Lake Lanao Operating Guide Curve.
2. AGUS 6 HEP, units 1 & 2 up-rated from 25 MW to 34.5 MW each and rated speed increased from 200 to 225 rpm effective February 1, 2020.
3. AGUS 2 HEP is limited to 120 MW total load to prevent risk of flooding at lakeshore areas and Balo-i plains as per Environmental Compliance Certificate dated January 14, 1992.
4. AGUS 5 HEP gate no. 2 clogged at 0.10m for Nawlach Pulp Inc. (NPI) plant water use.
5. The usual occurrence of Peak is at 1800H.
6. Forecast inflow of Lake Lanao is stable and operating at Normal Stage.
7. Agus 6 HEP: 18cms of water spilled due to partially opened spillway gate no. 1.
Prepared by: |  |  | Checked and Reviewed by: |  |  | Checked and Reviewed by: |  | Approved by:
O.M. LAVA |  |  | JMM MATA |  |  | EL ADIONG |  | C.C. AMIGABLE JR.
Prin. Engr. A, GPD |  |  | Manager, GPD |  |  | Acting Manager, GPD |  | Dept. Manager, GPD
Prepared by: |  |  | Checked and Reviewed by: |  |  | Checked and Reviewed by: |  | Approved by:
D.R.B. CAIRO |  |  | JMM MATA |  |  | EL ADIONG |  | DB ESMADE JR.
Prin. Engr. B, GPD |  |  | Manager, GPD |  |  | OIC-Dept Manager, GPD |  | Acting Dept. Manager, GPD
Agus 2 HEP is limited to 40 MW/per unit due to water constraints as per Environmental Compliance Certificate "that Agus 2 shall not be operated at full capacity..." This is to prevent risk of flooding at lakeshore areas and Baloi plains.
AGUS 1 | 80 | 80 | 0
AGUS 2 | 180 | 180 | 120
AGUS 4 | 158.1 | 158.1 | 105.4
AGUS 5 | 55 | 55 | 55
AGUS 6 | 219 | 219 | 165
AGUS 7 | 54 | 54 | 54
PULANGI IV | 255 | 255 | 215